# SOP-EL-014: Electrical isolation (LOTO) and restart of LT motor-driven pumps – A2/A2B

| Document number | SOP-EL-014 |
| --- | --- |
| Revision | 3 |
| Effective date | 2025-11-02 |
| Status | CURRENT |
| Department | Electrical |
| Classification | INTERNAL |
| Applicable assets | A2 (01-A2A), A2B, M-A2, MCC-2-F07, XV-2041, XV-2043 |

This revision supersedes SOP-EL-014 Rev 2. Discharge isolation valve retagged to XV-2043 per MOC-2025-118. Zero-energy verification moved before breaker rack-out.

## 1. Purpose

To define the safe electrical isolation (Lock-Out / Tag-Out) and restart of LT (415 V) motor-driven pumps A2 / A2B in CDU-1, fed from MCC-2 (A2: feeder MCC-2-F07).

## 2. Scope

Applies to Electrical and Operations personnel of CDU-1. Covers pump A2 (motor M-A2, 45 kW nameplate per DS-CDU-A2, 415 V, FLA 78 A) and standby pump A2B.

## 3. Safety requirements / PPE

Arc-flash rated face shield and FR coverall for racking operations.

Insulated gloves (Class 0) and 1000 V rated tester; test the tester on a known live source.

Never bypass the PTW system. Two-person rule at MCC-2.

## 4. Procedure

Obtain an electrical isolation Permit-to-Work (PTW) from the CDU-1 Shift In-charge. Confirm pump A2 is stopped and standby pump A2B is running.

Inform the CDU-1 panel operator and record the isolation request in the shift log.

Operations to close suction valve XV-2041 and discharge isolation valve XV-2043; apply valve locks and tags.

At MCC-2, switch OFF the breaker of feeder MCC-2-F07 (motor M-A2).

BEFORE racking out the breaker, verify zero energy at the motor terminal box of M-A2 using an approved 1000 V rated tester (live-dead-live check).

Rack out the feeder MCC-2-F07 breaker to TEST position.

Apply personal padlock and 'DO NOT OPERATE' tag at MCC-2-F07 using a LOTO hasp; remove control fuses. Record lock numbers in the LOTO register.

Carry out try-out: press START at the local control station (LCS) and confirm the motor does not start. Return LCS to STOP.

Discharge residual energy / apply portable earth at the terminal box if work on terminals is required.

Carry out troubleshooting per TG-A2 Rev 2 (seal, overload, NPSH, vibration checks). Check O/L relay setting against SLD-MCC-2 current revision.

On completion remove earths and tools, close terminal box, IR test motor (>= 1 MOhm at 500 V), remove locks and tags in reverse order, rack in breaker to SERVICE.

Return PTW. Operations open XV-2041, prime pump, start A2 and open XV-2043 gradually; confirm running current <= 78 A FLA and vibration < 4.5 mm/s.

## 5. Approval

| Role | Name | Signature | Date |
| --- | --- | --- | --- |
| Prepared | D. Menon, Electrical Engineer | (signed) | 2025-11-02 |
| Reviewed | N. Kamath, Safety Officer | (signed) | 2025-11-02 |
| Approved | M. Patil, Head - Electrical | (signed) | 2025-11-02 |

## 6. Revision history

| Rev | Date | Description | Approved by |
| --- | --- | --- | --- |
| 0 | 2018-02-20 | First issue | M. Patil |
| 1 | 2020-07-01 | Added try-out step at LCS | M. Patil |
| 2 | 2023-04-10 | Updated PPE; valve tags per PID-CDU-03 Rev B | M. Patil |
| 3 | 2025-11-02 | Zero-energy verification at terminal box moved BEFORE rack-out; discharge valve XV-2043 per PID-CDU-03 Rev C / MOC-2025-118 | M. Patil |